# Servicing Gas Furnace

Name_____________________________________ date_________________

Make________________________

Mod________________________________  Serial_______________________

1.  Check tstat for level and tight against wall, set above room temp

- Check filter

- Flame safety control

  - Pilot, check flame, clean

  - Check pilot dropout

  - Check for pilot valve leakage after dropout

  - HSI, check for hot spots

  - Check HSI ohms.  Above 150 ohms recommend replace

  - Check flame rod microamps

  - Remove and clean flame rod, recheck microamps

  - Shut off gas, check flame safety dropouts

- Burners, clean

- Check heat exchanger for cracks

- Fire off main burners, adjust, check for flame change when circ fan starts

- Check draft hood with match for proper draft

- Check amp draw of circ fan motor, check cap

- Check motor and fan bearing condition

- Check belt

- Check/clean circ fan blower wheel and motor (if 90% furnace, check secondary heat exchanger for dirt)

- Oil circ fan motor and blower

- Clean return plenum

- Check amp draw of inducer, oil bearings

- If 2 stage, fire off 2d stage, check amp draw of inducer

- Check delta T

- Check limit by stopping circ fan

- Check operation of press switch, centrifugal switch, etc

- If condensing furnace, clean condensate drain

- Check metal vent for rust

- Check for gas leaks

- Make sure furnace is running when leaving mechanical room